## Use Cases Evaluation Sessions
UMAR use cases text-based
# | Use Case | Inputs | Use Case #
1 | At least one setpoint per zone. Nest preference (warning) | brick:Zone brick:hasPart brick:Valve | 1
2 | Each command (e.g. valve command) needs to have the corresponding equipment (valve) linked. | brick:Valve_Command brick:Valve brick:isPointOf | 13
3 | At least one sensor per energy zone (Energy Zone = UMAR unit). Nest preference (warning) | brick:Energy_Zone brick:hasPart brick:Sensor | 3
4 | If a media (electricity) in a building exists, at least one building meter for this media per UMAR unit (= Energy Zone) needs to exist as well. This leads to: At least one building electrical meter per HVAC zone. Nest preference (warning) | brick:Energy_Zone brick:Building_Electrical_Meter brick:hasPart | 4
5 | One zone has at least one space. Global constraint (violation). | brick:Zone brick:isLocationOf brick:Space | 10
6 | A meter exists only with at least one sensor. Nest preference (warning) | brick:Meter brick:hasPart brick:Sensor | 11
7 | Every sensor needs a unit. Global constraint (violation). | brick:Sensor brick:hasUnit | 14
8 | The building's primary function needs to be added for a NEST unit (=building). Nest preference (warning) | brick:Building brick:Building_Primary_Function ( "Adult Education"^^xsd:string "Ambulatory Surgical Center"^^xsd:string....) ; | 18
9 | Each temperature setpoint needs to have a temperature. Global constraint (violation). | brick:Temperature_Setpoint brick:Temperature xsd:nonNegativeInteger | 19
10 | Each temperature must have Celcius or Farenheit as logical unit. Global constraint (violation). | brick:Temperature brick:hasUnit unit:DEG_C unit:DEG_F | 20
UMAR use cases ShapeVOWL
# | Use Case | Inputs | Use Case #
1 | A sensor cannot be connected to Brick entity "outside". Nest preference (warning) | brick:Sensor brick:Outside brick:isPartOf | 5
2 | At least one sensor per HVAC zone (HVAC Zone = UMAR room). Nest preference (warning) | brick:HVAC_Zone brick:hasPart brick:Sensor | 3
3 | If a media (water) in a building exists, at least one building meter for this media per UMAR room (=HVAC Zone) needs to exist as well. This leads to: At least one building water meter per HVAC zone. Nest preference (warning) | brick:HVAC_Zone brick:Building_Water_Meter brick:hasPart | 4
4 | One building meter must be linked to one NEST unit. Nest preference (warning) | brick:Building_Meter brick:hasLocation brick:Building | 9
5 | All zones need to be within a NEST unit. Nest preference (warning) | brick:Zone brick:hasLocation brick:Building | 7
6 | If a setpoint exists a corresponding sensor needs to exist and be linked. Global constraint (violation). | brick:Setpoint brick:hasPoint brick:Sensor | 12
7 | Every setpoint needs a unit. Global constraint (violation). | brick:Setpoint brick:hasUnit | 15
8 | The construction year needs to be added for a NEST unit (=building). Nest preference (warning) | brick:Building brick:Building_Primary_Function xsd:nonNegativeInteger | 16
9 | Each building needs to have an area. Global constraint (violation). | brick:Building brick:area | 19
10 | Each area must have ft2 or m2 as logical unit or numeric value. Global constraint (violation). | brick:area brick:hasUnit unit:FT2 unit:M2 | 20